{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["预防性试验清单"],"read":"whole","date_system":"1900"}

{"sheet":"预防性试验清单","index":0,"n_rows":88,"n_cols":31,"rows_kept":88,"merged":[[0,0,0,30],[1,0,2,1],[1,2,2,6],[1,7,1,12],[1,13,2,15],[1,16,2,17],[1,18,2,21],[1,22,2,25],[1,26,2,27],[1,28,2,28],[1,29,2,29],[1,30,2,30],[2,7,2,11],[3,0,3,1],[3,2,3,6],[3,7,3,11],[3,13,3,15],[3,16,3,17],[3,18,3,21],[3,22,3,25],[3,26,3,27],[4,0,5,1],[4,2,5,6],[4,7,4,11],[4,13,5,15],[4,16,5,17],[4,18,5,21],[4,22,5,25],[4,26,5,27],[4,28,5,28],[4,29,5,29],[5,7,5,11],[6,0,6,1],[6,2,6,6],[6,7,6,11],[6,13,6,15],[6,16,6,17],[6,18,6,21],[6,22,6,25],[6,26,6,27],[7,0,7,1],[7,2,7,6],[7,7,7,11],[7,13,7,15],[7,16,7,17],[7,18,7,21],[7,22,7,25],[7,26,7,27],[8,0,8,1],[8,2,8,6],[8,7,8,11],[8,13,8,15],[8,16,8,17],[8,18,8,21],[8,22,8,25],[8,26,8,27],[9,0,9,1],[9,2,9,6],[9,7,9,11],[9,13,9,15],[9,16,9,17],[9,18,9,21],[9,22,9,25],[9,26,9,27],[10,0,10,11],[10,13,10,15],[10,16,10,17],[10,18,10,21],[10,22,10,25],[10,26,10,27],[11,0,11,30],[12,0,12,2],[12,3,12,30],[13,1,13,2],[13,3,13,4],[13,5,13,8],[13,9,13,14],[13,16,13,20],[13,21,13,22],[13,23,13,26],[13,27,13,29],[14,0,15,0],[14,1,15,2],[14,3,15,4],[14,5,15,8],[14,9,15,14],[14,16,15,20],[14,21,15,22],[14,23,15,26],[14,27,15,29],[16,1,16,2],[16,3,16,4],[16,5,16,8],[16,9,16,14],[16,16,16,20],[16,21,16,22],[16,23,16,26],[16,27,16,29],[17,1,17,2],[17,3,17,4],[17,5,17,8],[17,9,17,14],[17,16,17,20],[17,21,17,22],[17,23,17,26],[17,27,17,29],[18,1,18,2],[18,3,18,4],[18,5,18,8],[18,9,18,14],[18,16,18,20],[18,21,18,22],[18,23,18,26],[18,27,18,29],[19,1,19,2],[19,3,19,4],[19,5,19,8],[19,9,19,14],[19,16,19,20],[19,21,19,22],[19,23,19,26],[19,27,19,29],[20,1,20,2],[20,3,20,4],[20,5,20,8],[20,9,20,14],[20,16,20,20],[20,21,20,22],[20,23,20,26],[20,27,20,29],[21,1,21,2],[21,3,21,8],[21,9,21,14],[21,16,21,20],[21,21,21,22],[21,23,21,26],[21,27,21,29],[22,0,22,30],[23,0,23,30],[24,0,25,5],[24,6,25,8],[24,9,25,12],[24,13,25,24],[24,25,25,30],[26,0,26,1],[26,2,26,3],[26,4,26,5],[26,6,26,8],[26,9,26,12],[26,13,26,14],[26,15,26,21],[26,22,26,24],[26,25,26,27],[26,28,26,29],[27,0,28,1],[27,2,28,3],[27,4,28,5],[27,6,28,8],[27,9,28,12],[27,13,27,14],[27,15,27,21],[27,22,28,24],[27,25,28,27],[27,28,28,29],[28,13,28,14],[28,15,28,21],[29,0,29,1],[29,2,29,3],[29,4,29,5],[29,6,29,8],[29,9,29,12],[29,13,29,14],[29,15,29,21],[29,22,29,24],[29,25,29,27],[29,28,29,29],[30,0,30,1],[30,2,30,3],[30,4,31,5],[30,6,30,8],[30,9,30,12],[30,13,31,14],[30,15,31,21],[30,22,30,24],[30,25,30,27],[30,28,30,29],[31,0,31,1],[31,2,31,3],[31,6,31,8],[31,9,31,12],[31,22,31,24],[31,25,31,27],[31,28,31,29],[32,0,32,1],[32,2,32,3],[32,4,32,5],[32,6,32,8],[32,9,32,12],[32,13,32,14],[32,15,32,21],[32,22,32,24],[32,25,32,27],[32,28,32,29],[33,0,33,1],[33,2,33,3],[33,4,33,5],[33,6,33,8],[33,9,33,12],[33,13,33,14],[33,15,33,21],[33,22,33,24],[33,25,33,27],[33,28,33,29],[34,0,34,1],[34,2,34,3],[34,4,34,5],[34,6,34,8],[34,9,34,12],[34,13,34,14],[34,15,34,21],[34,22,34,24],[34,25,34,27],[34,28,34,29],[35,0,35,1],[35,2,35,3],[35,4,35,5],[35,6,35,8],[35,9,35,12],[35,13,35,14],[35,15,35,21],[35,22,35,24],[35,25,35,27],[35,28,35,29],[36,0,36,1],[36,2,36,3],[36,4,36,8],[36,9,36,12],[36,13,36,14],[36,15,36,21],[36,22,36,24],[36,25,36,27],[36,28,36,29],[37,0,37,30],[38,0,38,8],[38,9,38,30],[39,0,39,2],[39,3,39,30],[40,0,40,1],[40,2,40,3],[40,4,40,5],[40,6,40,9],[40,10,40,12],[40,13,40,14],[40,15,40,21],[40,22,40,24],[40,25,40,27],[40,28,40,29],[41,0,42,1],[41,2,42,3],[41,4,42,5],[41,6,42,9],[41,10,42,12],[41,13,41,14],[41,15,42,21],[41,22,42,24],[41,25,42,27],[41,28,42,29],[42,13,42,14],[43,0,43,1],[43,2,43,3],[43,4,43,5],[43,6,43,9],[43,10,43,12],[43,13,43,14],[43,15,43,21],[43,22,43,24],[43,25,43,27],[43,28,43,29],[44,0,44,1],[44,2,44,3],[44,4,45,5],[44,6,44,9],[44,10,44,12],[44,13,45,14],[44,15,45,21],[44,22,44,24],[44,25,44,27],[44,28,44,29],[45,0,45,1],[45,2,45,3],[45,6,45,9],[45,10,45,12],[45,22,45,24],[45,25,45,27],[45,28,45,29],[46,0,46,1],[46,2,46,3],[46,4,46,5],[46,6,46,9],[46,10,46,12],[46,13,46,14],[46,15,46,21],[46,22,46,24],[46,25,46,27],[46,28,46,29],[47,0,47,1],[47,2,47,3],[47,4,47,5],[47,6,47,9],[47,10,47,12],[47,13,47,14],[47,15,47,21],[47,22,47,24],[47,25,47,27],[47,28,47,29],[48,0,48,1],[48,2,48,3],[48,4,48,5],[48,6,48,9],[48,10,48,12],[48,13,48,14],[48,15,48,21],[48,22,48,24],[48,25,48,27],[48,28,48,29],[49,0,49,1],[49,2,49,3],[49,4,49,5],[49,6,49,9],[49,10,49,12],[49,13,49,14],[49,15,49,21],[49,22,49,24],[49,25,49,27],[49,28,49,29],[50,0,50,1],[50,2,50,3],[50,4,50,9],[50,10,50,12],[50,13,50,14],[50,15,50,21],[50,22,50,24],[50,25,50,27],[50,28,50,29],[51,0,51,30],[52,0,52,9],[52,10,52,30],[53,0,54,4],[53,5,54,8],[53,9,54,12],[53,13,54,23],[53,24,54,30],[55,1,55,2],[55,3,55,4],[55,5,55,7],[55,8,55,12],[55,13,55,14],[55,15,55,20],[55,21,55,22],[55,23,55,26],[55,27,55,29],[56,0,57,0],[56,1,57,2],[56,3,57,4],[56,5,57,7],[56,8,57,12],[56,13,56,14],[56,15,57,20],[56,21,57,22],[56,23,57,26],[56,27,57,29],[57,13,57,14],[58,1,58,2],[58,3,58,4],[58,5,58,7],[58,8,58,12],[58,13,58,14],[58,15,58,20],[58,21,58,22],[58,23,58,26],[58,27,58,29],[59,1,59,2],[59,3,60,4],[59,5,59,7],[59,8,59,12],[59,13,60,14],[59,15,60,20],[59,21,59,22],[59,23,59,26],[59,27,59,29],[60,1,60,2],[60,5,60,7],[60,8,60,12],[60,21,60,22],[60,23,60,26],[60,27,60,29],[61,1,61,2],[61,3,61,4],[61,5,61,7],[61,8,61,12],[61,13,61,14],[61,15,61,20],[61,21,61,22],[61,23,61,26],[61,27,61,29],[62,1,62,2],[62,3,62,4],[62,5,62,7],[62,8,62,12],[62,13,62,14],[62,15,62,20],[62,21,62,22],[62,23,62,26],[62,27,62,29],[63,1,63,2],[63,3,63,4],[63,5,63,7],[63,8,63,12],[63,13,63,14],[63,15,63,20],[63,21,63,22],[63,23,63,26],[63,27,63,29],[64,1,64,2],[64,3,64,4],[64,5,64,7],[64,8,64,12],[64,13,64,14],[64,15,64,20],[64,21,64,22],[64,23,64,26],[64,27,64,29],[65,1,65,2],[65,3,65,7],[65,8,65,12],[65,13,65,14],[65,15,65,20],[65,21,65,22],[65,23,65,26],[65,27,65,29],[66,0,66,30],[67,0,67,10],[67,11,67,30],[68,0,68,10],[68,11,68,13],[68,14,68,24],[68,25,68,30],[69,1,69,2],[69,3,69,4],[69,5,69,9],[69,10,69,13],[69,15,69,20],[69,21,69,22],[69,23,69,26],[69,27,69,29],[70,0,71,0],[70,1,71,2],[70,3,71,4],[70,5,71,9],[70,10,71,13],[70,15,71,20],[70,21,71,22],[70,23,71,26],[70,27,71,29],[72,1,72,2],[72,3,72,4],[72,5,72,9],[72,10,72,13],[72,15,72,20],[72,21,72,22],[72,23,72,26],[72,27,72,29],[73,1,73,2],[73,3,73,4],[73,5,73,9],[73,10,73,13],[73,15,73,20],[73,21,73,22],[73,23,73,26],[73,27,73,29],[74,1,74,2],[74,3,74,4],[74,5,74,9],[74,10,74,13],[74,15,74,20],[74,21,74,22],[74,23,74,26],[74,27,74,29],[75,1,75,2],[75,3,75,9],[75,10,75,13],[75,15,75,20],[75,21,75,22],[75,23,75,26],[75,27,75,29],[76,0,76,30],[77,0,77,10],[77,11,77,30],[78,0,78,10],[78,11,78,13],[78,14,78,24],[78,25,78,30],[79,1,79,2],[79,3,79,4],[79,5,79,9],[79,10,79,13],[79,15,79,20],[79,21,79,22],[79,23,79,26],[79,27,79,29],[80,0,81,0],[80,1,81,2],[80,3,81,4],[80,5,81,9],[80,10,81,13],[80,15,81,20],[80,21,81,22],[80,23,81,26],[80,27,81,29],[82,1,82,2],[82,3,82,4],[82,5,82,9],[82,10,82,13],[82,15,82,20],[82,21,82,22],[82,23,82,26],[82,27,82,29],[83,1,83,2],[83,3,83,4],[83,5,83,9],[83,10,83,13],[83,15,83,20],[83,21,83,22],[83,23,83,26],[83,27,83,29],[84,1,84,2],[84,3,84,4],[84,5,84,9],[84,10,84,13],[84,15,84,20],[84,21,84,22],[84,23,84,26],[84,27,84,29],[85,1,85,2],[85,3,85,4],[85,5,85,9],[85,10,85,13],[85,15,85,20],[85,21,85,22],[85,23,85,26],[85,27,85,29],[86,1,86,2],[86,3,86,4],[86,5,86,9],[86,10,86,13],[86,15,86,20],[86,21,86,22],[86,23,86,26],[86,27,86,29],[87,1,87,2],[87,3,87,9],[87,10,87,13],[87,15,87,20],[87,21,87,22],[87,23,87,26],[87,27,87,29],[88,0,88,30],[89,0,89,30]]}
["芜湖远恒资产运营有限公司配电房现勘情况"]
["序号","","单位名称","","","","","变压器","","","",null,null,"低压柜\n数量","","","高压柜数量","","母线","","","","电缆","","","","接地网","","继电\n保护","断路\n器","备注"]
[null,"",null,"","","","","规格","","","",null,"数量/台",null,"","",null,"",null,"","","",null,"","","",null,""]
[1,1,"水务局大楼","","","","","400kVA 箱变","","","",null,1,3,3,3,2,2,"10KV1 组","","","","10KV1 根","","","","1 处",""]
[2,2,"皖江金融大厦","","","","","630kVA","","","",null,1,14,14,14,6,6,"10KV1 组","","","","10KV2 根","","","","1 处","",4,4]
[null,"",null,"","","","","800kVA","","","",null,1,null,"","",null,"",null,"","","",null,"","","",null,""]
[3,3,"皖江电子商务中心","","","","","400kVA","","","",null,2,10,10,10,7,7,"10KV1 组","","","","10KV2 根","","","","1 处","",3,3]
[4,4,"九华中路 116 号","","","","","1000kVA","","","",null,1,5,5,5,4,4,"10KV1 组","","","","10KV1 根","","","","1 处","",2,2]
[5,5,"联航大楼","","","","","200kVA","","","",null,1,6,6,6,null,"",null,"","","","10KV2 根","","","","1 处",""]
[6,6,"能源大楼","","","","","160kVA 箱变+200kVA 箱变","","","",null,2,10,5,5,4,2,"10KV2 组","","","","10KV2 根","","","","2 处",""]
["合计","",null,"","","","",null,"","","",null,9,48,43,43,23,21,"6 组","","","","10 根","","","","7 处","",9,9]
["预防性试验清单（水务局造价）",{"$nulls":3},"",null,"",null,"",null,"",{"$nulls":3},"",{"$nulls":5},"",{"$nulls":3},"",""]
[]
["序号","电压\n等级",null,"设备名称","","试验设备","",null,"","检修内容","",{"$nulls":3},"","数量","单位",{"$nulls":4},"检修\n周期",null,"国网执行标准","","",null,"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器","","变压器\n1250kva\n1250kva\n2000kva","",null,"","（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电阻、吸\n收比；\n（ 3）绕组连同套管的交流耐压试验；","",{"$nulls":3},"",1,"台",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":4},"",null,"",null,"",null,"",{"$nulls":3},"",0,{"$nulls":8},"","",{"$nulls":4},"800~2000kva"]
[2,"10kV",null,"电力电缆","","电力电缆","",null,"","(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄漏电流测\n量；","",{"$nulls":3},"",1,"条",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",null,"高压柜",null,"负荷开关","",null,"","(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相对地）；\n","",{"$nulls":3},"",{"$nulls":6},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[4,"10kV",null,"高压母线","","母线","",null,"","（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试验。","",{"$nulls":3},"",1,"组",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组"]
[5,"10kV",null,"接地装置","","接地装置","",null,"","测量接地系统的接地电阻。","",{"$nulls":3},"",1,"组",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[6,"10kV",null,"低压柜","","低压柜","",null,"","(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验","",{"$nulls":3},"",3,"台",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[7,null,null,"清障、清灰","",null,"",null,"","电力设备清灰、现场箱变有树木，春季易燃 ，风险较大，\n需要清理。","",{"$nulls":3},"",1,"处",{"$nulls":4},"一年",null,null,"",""]
[]
["预防性试验清单（皖江金融大厦造价）",{"$nulls":7},"",null,"",{"$nulls":3},"",{"$nulls":5},"",{"$nulls":3},""]
[{"$nulls":14},"",{"$nulls":5},"",{"$nulls":3},""]
[{"$nulls":14},"",{"$nulls":5},"",{"$nulls":3},""]
["号序",null,"电压\n等级",null,"设备名称",null,"试验设备",null,"","检修内容","",null,null,"量数","","位单",{"$nulls":6},"检修\n周期",null,"","国网执行标准",null,null,"达成效果",null,"备注"]
[1,null,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",null,"","    （ 1）测量绕组的直流电阻；\n    （ 2）测量绕组连同套管的绝\n     缘电阻、吸收比\n    （ 3）绕组连同套管的交流耐\n     压试验；\n    ","",null,null,1,1,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"800kva 以下"]
[{"$nulls":8},"",null,"",null,null,1,1,{"$nulls":9},"",{"$nulls":5},"800~2000kva"]
[2,null,"10kV",null,"电力电缆",null,"电力电缆",null,"","     (1)测量绝缘电阻；\n     (2)非破坏性直流耐压试验及\n     泄漏电流测量；","",null,null,2,2,"条",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一次/根"]
[3,null,"10kV",{"$nulls":3},"断路器",null,"","     (1)测量绝缘电阻；\n     (2)交流耐压试验（断口、相\n     对地）；\n     (3)测量每相导电回路的电\n     阻；\n   ","",{"$nulls":11},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[4,null,"10kV",{"$nulls":3},"隔离手车",null,"","     (1)测量绝缘电阻；\n     (2)交流耐压试验。","",{"$nulls":11},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[5,null,"10kV",null,"高压母线",null,"母线",null,"","    （ 1）测量绝缘电阻；\n    （ 2）连同套管的交流耐压试 验。","",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一组"]
[6,null,"10kV",null,"接地装置",null,"接地装置",null,"","测量接地系统的接地电阻。","",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[7,null,"10kV",null,"继电保护",null,"继电保护装置",null,"","    （ 1）保护整定值校核；\n    （ 2）整组保护的模拟联跳试\n     验。","",null,null,4,4,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[8,null,"10kV",null,"低压柜",null,"低压柜",null,"","     (1)绝缘电阻试验\n     (2)耐压试验\n     (3)整组联动试验","",null,null,14,14,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[9,{"$nulls":3},"清障、清灰",{"$nulls":3},""," 电力设备清灰、  现场箱变有树木，春季易燃，\n     风险较大 ，需要清理。","",null,null,1,0,"处",{"$nulls":6},"一年",null,""]
[]
[{"$nulls":8},"","预防性试验清单（皖江电子商务中心造价）",{"$nulls":4},"",{"$nulls":9},""]
[{"$nulls":3},"       ",{"$nulls":4},"",{"$nulls":5},"",{"$nulls":9},""]
["序号",null,"电压\n等级",null,"设备名称",null,"试验设备",null,"",null,"检修内容",null,null,"数量","","单位",{"$nulls":6},"检修\n周期",null,"","国网执行标准",null,null,"达成效果",null,"备注"]
[1,null,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",null,"",null,"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝\n缘电阻、吸收比\n（ 3）绕组连同套管的交流耐\n压试验；\n",null,null,2,2,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"800kva 以下"]
[{"$nulls":8},"",{"$nulls":4},0,0,{"$nulls":9},"",{"$nulls":5},"800~2000kva"]
[2,null,"10kV",null,"电力电缆",null,"电力电缆",null,"",null,"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及\n泄漏电流测量；",null,null,2,2,"条",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一次/根"]
[3,null,"10kV",{"$nulls":3},"断路器",null,"",null,"(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相\n对地）；\n(3)测量每相导电回路的电\n阻；\n",{"$nulls":3},"",{"$nulls":7},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[4,null,"10kV",{"$nulls":3},"隔离手车",null,"",null,"(1)测量绝缘电阻；\n(2)交流耐压试验。",{"$nulls":3},"",{"$nulls":7},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[5,null,"10kV",null,"高压母线",null,"母线",null,"",null,"（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试\n验。",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一组"]
[6,null,"10kV",null,"接地装置",null,"接地装置",null,"",null,"测量接地系统的接地电阻。",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[7,null,"10kV",null,"继电保护",null,"继电保护装置",null,"",null,"（ 1）保护整定值校核；\n（ 2）整组保护的模拟联跳试验。",null,null,3,3,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[8,null,"10kV",null,"低压柜",null,"低压柜",null,"",null,"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",null,null,10,10,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[9,{"$nulls":3},"清障、清灰",{"$nulls":3},"",null,"电力设备清灰、现场箱变有树木，春季易燃，\n风险较大 ，需要清理。",null,null,1,0,"处",{"$nulls":6},"一年",null,""]
[]
[{"$nulls":10},"预防性试验清单（九华中路 116 号造价）",{"$nulls":3},""]
[]
[]
["序号","电压\n等级",null,"设备名称",null,"试验设备",null,null,"检修内容",{"$nulls":4},"数量","","单位",{"$nulls":5},"检修\n周期",null,"国网执行标准",{"$nulls":3},"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",null,null,"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电\n阻、吸收比\n（ 3）绕组连同套管的交流耐压试\n验；\n",{"$nulls":4},0,0,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":13},1,1,{"$nulls":15},"800~2000kva"]
[2,"10kV",null,"电力电缆",null,"电力电缆",null,null,"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄漏\n电流测量；",{"$nulls":4},1,1,"条",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",{"$nulls":3},"断路器/负荷\n开关",null,null,"(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相对地）；\n(3)测量每相导电回路的电阻；\n",{"$nulls":12},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[4,"10kV",{"$nulls":3},"隔离手车",null,null,"(1)测量绝缘电阻；\n(2)交流耐压试验。",{"$nulls":12},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[5,"10kV",null,"高压母线",null,"母线",null,null,"（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试验。",{"$nulls":4},1,1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组"]
[6,"10kV",null,"接地装置",null,"接地装置",null,null,"测量接地系统的接地电阻。",{"$nulls":4},1,1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[7,"10kV",null,"继电保护",null,"继电保护装\n置",null,null,"（ 1）保护整定值校核；\n（ 2）整组保护的模拟联跳试验。",{"$nulls":4},2,2,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[8,"10kV",null,"低压柜",null,"低压柜",null,null,"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",{"$nulls":4},5,5,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[9,null,null,"清障、清灰",{"$nulls":4},"电力设备清灰、现场箱变有树木，春季易燃，风险\n较大 ，需要清理。",{"$nulls":4},1,0,"处",{"$nulls":5},"一年"]
[]
[{"$nulls":11},"预防性试验清单（联航大楼造价）"]
[]
["序号","电压\n等级",null,"设备名称",null,"试验设备",{"$nulls":4},"检修内容",{"$nulls":3},"数量","单位",{"$nulls":5},"检修\n周期",null,"国网执行标准",{"$nulls":3},"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",{"$nulls":4},"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电\n阻、吸收比\n（ 3）绕组连同套管的交流耐压试\n验；\n",{"$nulls":3},1,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":14},0,{"$nulls":15},"800~2000kva"]
[2,"10kV",null,"电力电缆",null,"电力电缆",{"$nulls":4},"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄\n漏电流测量；",{"$nulls":3},2,"条",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",null,"接地装置",null,"接地装置",{"$nulls":4},"测量接地系统的接地电阻。",{"$nulls":3},1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[4,"10kV",null,"低压柜",null,"低压柜",{"$nulls":4},"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",{"$nulls":3},6,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[5,null,null,"清障、清灰",{"$nulls":6},"电力设备清灰、现场箱变有树木，春季易燃 ，风\n险较大 ，需要清理。",{"$nulls":3},1,"处",{"$nulls":5},"一年"]
[]
[{"$nulls":11},"预防性试验清单（能源大楼造价）"]
[]
["序号","电压\n等级",null,"设备名称",null,"试验设备",{"$nulls":4},"检修内容",{"$nulls":3},"数量","单位",{"$nulls":5},"检修\n周期",null,"国网执行标准",{"$nulls":3},"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",{"$nulls":4},"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电\n阻、吸收比\n（ 3）绕组连同套管的交流耐压试\n验；\n",{"$nulls":3},1,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":14},0,{"$nulls":15},"800~2000kva"]
[2,"10kV",null,"电力电缆",null,"电力电缆",{"$nulls":4},"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄\n漏电流测量；",{"$nulls":3},1,"条",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",{"$nulls":3},"负荷开关",{"$nulls":4},"(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相对\n地）；\n",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[4,"10kV",null,"高压母线",null,"母线",{"$nulls":4},"（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试验。",{"$nulls":3},1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"一组"]
[5,"10kV",null,"接地装置",null,"接地装置",{"$nulls":4},"测量接地系统的接地电阻。",{"$nulls":3},1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[6,"10kV",null,"低压柜",null,"低压柜",{"$nulls":4},"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",{"$nulls":3},5,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[7,null,null,"清障、清灰",{"$nulls":6},"电力设备清灰、现场箱变有树木，春季易燃 ，风\n险较大 ，需要清理。",{"$nulls":3},1,"处",{"$nulls":5},"一年"]